## Slide 1: CE 3372 Water Systems Design
LeSSON 06 – Pumps and Lift Stations

## Slide 2: Overview
Pumps
  Description
  Suction Requirements
  System and Pump Curves

## Slide 3: Pumps

## Slide 4: Pumps
A mechanical device that transfers mechanical energy to move fluid
  Lift from lower to higher elevation Lift stations
  Increase pressure Booster stations

## Slide 6: Pumps
Positive Displacement Pumps
  Fixed volume of fluid is displaced each cycle regardless of static head/pressure
  Lower flow rates and higher head than non-positive pumps
Non-Positive Displacement Pumps (Centrifugal Pumps)
  Volume of fluid is dependent on static head/pressure in system (back pressure)
Notes: 2 principle types of plants

## Slide 7: Pumps
Positive Displacement Pumps
  Screw Pumps
  Reciprocating Pumps
Non-Positive Displacement Pumps
  Centrifugal (Radial-Flow) Pumps
  Propeller Pumps (Axial-Flow)
  Jet Pumps (Mixed-Flow)
Notes: 2 principle types of plants

## Slide 8: Positive Displacement Pumps
Screw Pump
  A revolving shaft with blades rotates in a trough at an incline and pushes water up
Notes: The auger catches a portion of water and lift it as the pump screw rotates.
The diameter, fill depth, pump angle, etc are determinants of pump charact.
Commonly used in wastewater lifting and hurricane barrier lifting
Very tolerant of debris in liquid. Failure is HUGE

## Slide 9: Positive Displacement Pumps
Reciprocating Pump
  A piston sucks the fluid into a cylinder and then pushes it out
Notes: Upstroke, chamber fills. Downstroke, liquid is pushed out
Check valves prevent back flow.
Bore diameter, stroke length and rate are principal det of the operating character of a piston pump.
If no flow can occur, discharge is blocked, piston pump can and will destroy !!

## Slide 10: Pumps
Positive Displacement Pumps
  Screw Pumps
  Reciprocating Pumps
Non-Positive Displacement Pumps
  Centrifugal (Radial-Flow) Pumps
  Propeller Pumps (Axial-Flow)
  Jet Pumps (Mixed-Flow)
Notes: 2 principle types of plants

## Slide 11: Non-Positive Displacement Pumps
Classification is based on the way water leaves the rotating part of the pump
  Radial-flow pump – water leaves impeller in radial direction
  Axial-flow pump – water leaves propeller in the axial direction
  Mixed-flow pump – water leaves impeller in an inclined direction (has both radial and axial components)
Notes: Propeller creates thrust
Impeller creates suction

## Slide 12: Radial-Flow Pumps
Centrifugal Pump
  Accelerates water using an impeller
https://www.youtube.com/watch?v=BaEHVpKc-1Q
https://www.youtube.com/watch?feature=player_detailpage&v=ECv1VwW6RTo#t=122
Discharge
Suction (Eye)
Notes: Play til 3:11
Rate of impeller is how much momentum it can transfer to the water
Conversion of rotational kinetic energy to hydrodynamic energy of fluid flow
Cent pump can be submersible wet or dry

## Slide 13: Axial Flow Pumps
Axial flow pumps have impellers whose axis of rotation is collinear with the discharge
Used in high flow, low head applications
suction
discharge
Notes: Moving the same axis the fan rotates on.
Collinear enough.
Perpendicular to blade

## Slide 14: Suction Requirements

## Slide 15: Suction Requirements
The most common cause of pumping failure is poor suction conditions
Cavitation occurs when liquid pressure is reduced to the vapor pressure of the liquid
For piping system with a pump, cavitation occurs when Pabs at the inflow falls below the vapor pressure of the water
Notes: They implode in such a great force and high heat and causes a lot of damage to pump
Reduce pump and impeller capacity

## Slide 16: Suction Requirements
Liquid must enter the pump eye under pressure; this pressure is called the Net Positive Suction Head available (NPSHa).
A centrifugal pump cannot lift water unless it is primed
  the first stage impellers must be located below the static HGL in the suction pit at pump start-up
Notes: They implode in such a great force and high heat and causes a lot of damage

## Slide 17: Suction Requirements
The manufacturer supplies a value for the minimum pressure the pump needs to operate.
This pressure is the Net Positive Suction Head required (NPSHr).
For proper pump operation (w/o cavitation)
  NPSHa> NPSHr
Notes: Draw NPSH example.
Required is by manufacturer
NPSHr must be maintained or exceeded!!
over all operating conditions, including start-up and shut-down.

## Slide 18: Suction Requirements
Available suction is computed from
Absolute pressure at liquid surface in suction pit
Absolute vapor pressure at liquid pumping temperature
Frictional head loss in inlet piping
Static elevation of the liquid above the pump inlet eye
Notes: VP cause of temperature
NPSH is pressure req at the suction of a pump to prevent cavitation
hs (static suction head): it is the difference in elevation between the suction liquid level and the centerline of the pump impeller.

## Slide 19: Suction Requirements
Example
Notes: MSL = mean sea level
Air pressure drops as you go up.
33.9 pressure = 1 atm water at standard
14.7 psi will hold up 33 feet of water. (12.7/14.7psi) is a ratio
85% real big thunderstorm. Atm is 85% of normal

## Slide 20: Suction Requirements
Example

## Slide 21: Suction Requirements
Example

## Slide 22: Suction Requirements
Example

## Slide 23: Suction Requirements
Example

## Slide 24: System and Pump Curves

## Slide 25: Selecting Pumps
Design conditions are specified
Pump is selected for the range of applications
A System Curve (H vs. Q) is prepared
System Curve is matched to Pump Curve
Matching point (Operating point) indicates the actual working conditions
Notes: Range of app (like needing to pump 120 MGPM)

## Slide 26: System Curves
A system (characteristic) curve is a plot of required head versus flow rate in a hydraulic system (H vs. Q)
  The curve depicts how much energy is necessary to maintain a steady flow under the supplied conditions
  Total head, Hp, = elevation head + head losses
Notes: System curve.. How much energy does it take to meet the needs of your system

## Slide 27: System Curves
Notes: The amount of head the pump must add to overcome elevation differences is dependent on system characteristics and topology (and independent of the pump discharge rate), and is referred to as static head or static lift. Friction and minor losses, however, are highly dependent on the rate of discharge through the pump. When these losses are added to the static head for a series of discharge rates, the resulting plot is called a system head curve".
  Apply the energy equation and incorporate various friction components

## Slide 28: System Curves
This relationship tells us that the added head has to be at least 30 meters just to keep the reservoirs at the two levels shown, if any flow is to occur the pump must supply more than 30 meters of head.

## Slide 29: Pump Curves
Provided information from the manufacturer on the performance of pumps in the form of curves.
Information may include:
  discharge on the x-axis
  head on the left y-axis
  pump power input on the right y-axis
  pump efficiency as a percentage
  speed of the pump (rpm)
  NPSH of the pump
Notes: Wire- ratio of electrical energy in to water energy out
  Added head versus discharge.
  Wire-to-water eﬃciency versus discharge.
  Mechanical power versus discharge.
  Net Positive Suction Head required versus discharge.
    the discharge on the x-axis,
    the head on the left y-axis,
    the pump power input on the right y-axis,
    the pump efficiency as a percentage,
    the speed of the pump (rpm = revolutions/min).
    the NPSH of the pump.

## Slide 30: Pump Curves
Provided d.
Notes:     Always read based on diameter of impeller, at a flow of _, head is
NPSH = total head on suction side
Amount req + amount available
Total dynamic head:
Head = Energy per unit weight of water
Energy = Kinetic + Potential
=velocity + (elevation + pressure)
    the discharge on the x-axis,
    the head on the left y-axis,
    the pump power input on the right y-axis,
    the pump efficiency as a percentage,
    the speed of the pump (rpm = revolutions/min).
    the NPSH of the pump.

## Slide 31: How to
Provided information from the manufacturer on the performance of pumps in the form of curves.
Information may include:
  discharge on the x-axis
  head on the left y-axis
  pump power input on the right y-axis
  pump efficiency as a percentage
  speed of the pump (rpm)
  NPSH of the pump
Notes: Wire- ratio of electrical energy in to water energy out
  Added head versus discharge.
  Wire-to-water eﬃciency versus discharge.
  Mechanical power versus discharge.
  Net Positive Suction Head required versus discharge.
    the discharge on the x-axis,
    the head on the left y-axis,
    the pump power input on the right y-axis,
    the pump efficiency as a percentage,
    the speed of the pump (rpm = revolutions/min).
    the NPSH of the pump.

## Slide 32: Pump Curves
  Pump A cannot meet the needs of the system at any flow rate
  Pump B supplies enough head over part of the system curve
  The shaded area is the area where the pump supplies excess head
Operating Point
Notes: System curve and pump curve are VERY important help select an appropriate pump or set of pumps.
System curve is how much head the SYSTEM needs to function
Pump curve is how much head the PUMP needs to function
Plot of pump curve and system curve
Can use a valve to throttle the system curve
So monster.. Head is pizzas (pizza becomes energy after you digest)
Poop factory with monsters
Pump Curve, you have Monster A and B (2 different people) who work together, based on pizzas
Monster B functions on pizzas at this rate and produces poop
And Monster A (system curve) also functions on pizzas at a different rate and produces poop
So if you feed them both the same, they produce the same.

## Slide 33
Notes: Look at the efficiency.
Pump is most efficient then

## Slide 34: Multiple Pumps
Series and parallel combinations can be used to adjust “pump curves” to fit system requirements.
Parallel pumps add flow for given head
Series pumps add head for given flow

## Slide 35
Notes: For pumps in parallel, the curve of two pumps, for example, is produced by adding the discharges of the two pumps at the same head (assuming identical pumps).

## Slide 36
H
Q
Q1
H1
H1
H1
2H1
H1
3H1
Single pump
Two pumps in series
Three pumps in series
Notes: For pumps in series, the curve of two pumps, for example, is produced by adding the heads of the two pumps at the same discharge.

## Slide 37: Next time
Multiple path pipelines (Networks)
  Network analysis by newton-raphson