## Slide 1: CE 3372 Water Systems Design
DRINKING WATER storage Part 2 (FALL 2020)

## Slide 2: Storage
Purpose of storage reservoirs
Types of reservoirs
Calculating storage requirements

## Slide 3: Storage Reservoirs
Equalizing or Operating Storage
  Equalize pumping rate into reservoirs
  Provide storage for peak demand times
  Provide system pressure without booster pumping
Fire and emergency pressures
Types
  Surface reservoirs
  Standpipes
  Elevated tanks

## Slide 4: Storage Compartments
Service storage
Emergency storage
Fire Storage
Emergency
Service
Fire

## Slide 5: Flow-equalization
Flow-equalization storage is sufficient storage to account for peak demands in the system without having to exceed supply capacity.
  A desirable volume is 1-2 days of average daily demand.

## Slide 6: Fire storage
Fire storage is sufficient storage to allow the system to meet routine uses plus substantial fire flow.
  The desirable volume is based on expected fire flow rates multiplied by the required fire flow duration.

## Slide 7: emergency storage
Emergency storage to allow the system to operate without external supply sources for a period of time to allow for repairs or other unusual circumstances.
  Without emergency storage, every upset will lead to a ”boil-water” order or substantial interruption of service — these kinds of interruptions should be rare if the system is well engineered.
  A desirable volume is 1-2 days of average daily demand.

## Slide 8: How much?
Engineering would tend to choose for the larger volumes
Economics will argue for the smaller volumes
  The engineer will have to balance these competing choices in a design.

## Slide 9: Residence time
Additionally, residence times in any storage reservoir for TREATED water should not exceed a reasonable amount disinfection residual contact time.
  For chlorine/chloramine disinfection time is on the order of 6-10 days
  Hydraulic retention time of any such reservoir should be no longer than 8 days (as a reasonable rule of thumb).

## Slide 10: Hydraulic Retention Time
Hydraulic retention time is the ratio of storage volume to average discharge through the reservoir

## Slide 11: Operating Storage
Determine hourly demand for design day
Calculate cumulative draft
Plot cumulative draft vs. time (24 hr)
Draw diagonal line representing constant pumping
Read required storage as sum of two maximum ordinates

## Slide 12: Mass Diagram (24-hr pumping)

## Slide 13: Mass Diagram (12-hr Pumping)

## Slide 17: Flow Equalization
The engineer needs to decide which demand to use:
  Daily
  Peak
These volumes are added to that needed for emergency and fire flow.
Determines the tank volume required
Tank type (elevated, at-grade, buried) determines shape – elevation, diameter, min-level, max-level.
  Elevated tanks have substantial structural considerations