## Slide 1: CE 3372 Water Systems Design
DRINKING WATER storage Part 1 (FALL 2020)

## Slide 2: Storage
Storage is used in water supply, storm water management, and wastewater systems for a variety of reasons.
  SERVICE STORAGE
    flow equalization — generally things are designed for a particular steady flow rate and storage can be used to accommodate variable flow rates in a system.
    Pressure zone maintenance
  EMERGENCY STORAGE
    used to provide supply during repairs and other system interrupts
  FIRE STORAGE
    used to provide supply during fire fighting activities – could logically be considered as part of emergency
Storage is either elevated (above grade), at grade (reservoir, tanks, ponds, etc.) or below grade (subsurface vaults — NOT AQUIFERS).

## Slide 3: Storage Compartments
Service storage
Emergency storage
Fire Storage
Emergency
Service
Fire

## Slide 4: Flow-equalization
Flow-equalization storage is sufficient storage to account for peak demands in the system without having to exceed supply capacity.
  A desirable volume is 1-2 days of average daily demand.

## Slide 5: Fire storage
Fire storage is sufficient storage to allow the system to meet routine uses plus substantial fire flow.
  The desirable volume is based on expected fire flow rates multiplied by the required fire flow duration.

## Slide 6: emergency storage
Emergency storage to allow the system to operate without external supply sources for a period of time to allow for repairs or other unusual circumstances.
  Without emergency storage, every upset will lead to a ”boil-water” order or substantial interruption of service — these kinds of interruptions should be rare if the system is well engineered.
  A desirable volume is 1-2 days of average daily demand.

## Slide 7: How much?
Engineering would tend to choose for the larger volumes
Economics will argue for the smaller volumes
  The engineer will have to balance these competing choices in a design.

## Slide 8: Residence time
Additionally, residence times in any storage reservoir for TREATED water should not exceed a reasonable amount disinfection residual contact time.
  For chlorine/chloramine disinfection time is on the order of 6-10 days
  An hydraulic retention time of any such reservoir should be no longer than 8 days (as a reasonable rule of thumb).

## Slide 9: Hydraulic Retention Time
Hydraulic retention time is the ratio of storage volume to average discharge through the reservoir

## Slide 10: How much? Flow Equalization
Operating (flow-equalization) storage is determined as follows:
  Determine the hourly demand for a typical design day.
  Compute the cumulative draft (cumulative volume as a function of time)
  Compute the average constant draft rate (flow rate that if applied over the day end at the same accumulated value)
  The equalization storage is the sum of the two largest deviations from the average flow line to the cumulative draft line.

## Slide 11: Service Storage
Purpose of storage reservoirs
Types of reservoirs
Calculating storage requirements

## Slide 12: Storage Reservoirs
Equalizing or Operating Storage
  Equalize pumping rate into reservoirs
  Provide storage for peak demand times
  Provide system pressure without booster pumping
Fire and emergency pressures
Types
  Surface reservoirs
  Standpipes
  Elevated tanks

## Slide 13: Surface Reservoirs
Where natural elevation is high enough
For inexpensive pumped storage
Covered for protection (contamination, algae growth, evaporation)
Good temperature control

## Slide 14: Standpipes
Vertical cylindrical pipe
Height > diameter
Useful storage = volume above elevation needed for minimum pressure
Low storage useful for emergencies
Steel, reinforced concrete

## Slide 15: Elevated Storage
Usually less $/volume of useful storage
Foundation design important
  Wind uplift
  Earthquake stress
General types
  Hemispherical bottom (50-75000 gal)
  Double ellipsoidal (< 1.5 MG)
  Radial cone bottom (up to 3 MG)
  Hydropillar (up to 3 MG)

## Slide 16: CB&I (formerly Chicago Bridge & Iron) Water Tanks

## Slide 17: Composite Elevated Tanks

## Slide 18: Hydropillar™

## Slide 19: Hydropillar

## Slide 20: Water Spheroids

## Slide 21: Standpipe Ground Level

## Slide 22: Standpipes and Reservoirs

## Slide 23: Freshmix™ Standpipe Mixing

## Slide 24: Composite Elevated Tanks
Standard CET Dimensions |  |  | 
Capacity (in U.S. gallons) | Tank Diameter (in feet) | Head Range (in feet) | Pedestal Diameter (in feet)
1,000,000 | 70 | 40 | 36
1,500,000 | 87 | 40 | 48
2,000,000 | 94 | 45 | 52
2,500,000 | 105 | 45 | 60
3,000,000 | 118 | 45 | 64

## Slide 25: Operating Storage
Determine hourly demand for design day
Calculate cumulative draft
Plot cumulative draft vs. time (24 hr)
Draw diagonal line representing constant pumping
Read required storage as sum of two maximum ordinates

## Slide 26: Mass Diagram (24-hr pumping)

## Slide 27: Mass Diagram (12-hr Pumping)

## Slide 31: Flow Equalization Storage
Demand pattern from historical data appropriate to the service area.

## Slide 32: Flow Equalization Storage
Accumulate the demand

## Slide 33: Flow Equalization Storage
Average constant draft

## Slide 34: Flow Equalization Storage
V1
V2
Sum the 2 largest deviations
Storage required V1+V2
In this chart, about 25000 volume units.

## Slide 35: Flow Equalization
The engineer needs to decide which demand to use:
  Daily
  Peak
These volumes are added to that needed for emergency and fire flow.
Determines the tank volume required
Tank type (elevated, at-grade, buried) determines shape – elevation, diameter, min-level, max-level.
  Elevated tanks have substantial structural considerations

## Slide 36: Typical installation

## Slide 37: Storm Water Storage
Used to mitigate peak flows from development.
Provide water quality benefit.
Develop a water resource (rainwater harvesting)

## Slide 38: Underground “tank”
More than a hole in the ground
  Needs structure to support surface loads
  Needs a way to drain completely (usually a pump)

## Slide 39: STORAGE IN COMPUTER MODELS
Storage elements in computer models are tanks or reservoirs (EPANET), or storage junctions (SWMM)
Have similar minimal data requirements that include:
  Invert (bottom) elevation
  Min Pool elevation (above the invert)
  Begin Pool elevation (above the invert)
  Max Pool elevation (above the invert)
  Tank dimensions (or depth-storage curve)

## Slide 40: Tank DESCRIPTIONS
Supply reservoir (or tank); identify reservoir pool elevation
  May need to make configuration assumptions
  Tank dimensions should be sensible
  Pipe length is given (or assumed based on min level and connecting node elevation)
Z=180 ft
Z=315 ft
Z=300 ft
L2=120 ft
L1=180 ft
Elevation
Max Level
Min Level
Diameter
Node 2
Pipe 8: L1 + L2 = 300 ft
Notes: Globe is most used.

## Slide 41: Tank DESCRIPTIONS
Supply reservoir (or tank); identify reservoir pool elevation
  Can also use a volume vs. depth table to convey tank storage capabilities -- quite similar to reservoir routing in hydrology
Z=180 ft
Z=315 ft
Z=300 ft
L2=120 ft
L1=180 ft
Elevation
Max Level
Min Level
Diameter
Node 2
Pipe 8: L1 + L2 = 300 ft
Notes: Globe is most used.