## Slide 1: CE 3372 Water Systems Design
Lecture 12: storage and extended period simulation

## Slide 2: Overview
Storage Concepts
  Flow equalization
EPANET Tank Model(s)
  Single period simulation
  But multiple period simulation -- interesting
Multiple Period Simulation
  Reasons
  Multiplier Table

## Slide 3: Storage
Storage is used in water supply, storm water management, and wastewater systems for a variety of reasons.
  One primary reason is flow equalization — generally things are designed for a particular steady flow rate and storage can be used to accommodate variable flow rates in a system.
Storage is either elevated (above grade), at grade (reservoir, tanks, ponds, etc.) or below grade (subsurface vaults — NOT AQUIFERS).

## Slide 4: Storage Compartments
Fire storage
Flow-equalization storage
Emergency storage
Emergency
Flow Equalization
Fire

## Slide 5: Fire storage
Fire storage is sufficient storage to allow the system to meet routine uses plus substantial fire flow.
  The desirable volume is based on expected fire flow rates multiplied by the required fire flow duration.

## Slide 6: Flow-equalization
Flow-equalization storage is sufficient storage to account for peak demands in the system without having to exceed supply capacity.
  A desirable volume is 1-2 days of average daily demand.

## Slide 7: emergency storage
Emergency storage to allow the system to operate without external supply sources for a period of time to allow for repairs or other unusual circumstances.
  Without emergency storage, every upset will lead to a ”boil-water” order or substantial interruption of service — these kinds of interruptions should be rare if the system is well engineered.
  A desirable volume is 1-2 days of average daily demand.

## Slide 8: How much?
Engineering would tend to choose for the larger volumes
Economics will argue for the smaller volumes
  The engineer will have to balance these competing choices in a design.

## Slide 9: Residence time
Additionally, residence times in any storage reservoir for TREATED water should not exceed a reasonable amount disinfection residual contact time.
  For chlorine/chloramine disinfection time is on the order of 6-10 days
  An hydraulic retention time of any such reservoir should be no longer than 8 days (as a reasonable rule of thumb).

## Slide 10: Hydraulic Retention Time
Hydraulic retention time is the ratio of storage volume to average discharge through the reservoir

## Slide 11: How much? Flow Equalization
Operating (flow-equalization) storage is determined as follows:
  Determine the hourly demand for a typical design day.
  Compute the cumulative draft (cumulative volume as a function of time)
  Compute the average constant draft rate (flow rate that if applied over the day end at the same accumulated value)
  The equalization storage is the sum of the two largest deviations from the average flow line to the cumulative draft line.

## Slide 12: Flow Equalization Storage
Demand pattern from historical data appropriate to the service area.

## Slide 13: Flow Equalization Storage
Accumulate the demand

## Slide 14: Flow Equalization Storage
Average constant draft

## Slide 15: Flow Equalization Storage
V1
V2
Sum the 2 largest deviations
Storage required V1+V2
In this chart, about 25000 volume units.

## Slide 16: Flow Equalization
The engineer needs to decide which demand to use:
  Daily
  Peak
These volumes are added to that needed for emergency and fire flow.
Determines the tank volume required
Tank type (elevated, at-grade, buried) determines shape – elevation, diameter, min-level, max-level.
  Elevated tanks have substantial structural considerations

## Slide 17: Typical installation

## Slide 18: Storm Water Storage
Used to mitigate peak flows from development.
Provide water quality benefit.
Develop a water resource (rainwater harvesting)

## Slide 19: Underground “tank”
More than a hole in the ground
  Needs structure to support surface loads
  Needs a way to drain completely (usually a pump)

## Slide 20: Readings
EPA NET User Manual – how to model storage tanks in a water distribution system.
  Interesting web-resources
    http://www.invisiblestructures.com/rainstore3.html
    http://www.upout.com/blog/san-francisco-3/heres-what-it-looks-like-under-those-brick-circles-in-the-street

## Slide 21: Recall earlier example

## Slide 22: Modeling Protocol
Sketch a layout on paper
Identify pipe diameters; length; roughness values
Identify node elevations; demands
Supply reservoir (or tank); identify reservoir pool elevation
Identify pumps; pump curve in problem units
Notes: Globe is most used.

## Slide 23: Tank
Supply reservoir (or tank); identify reservoir pool elevation
  May need assumptions
  Tank dimensions should be sensible
  Pipe length is given
Z=180 ft
Z=315 ft
Z=300 ft
L2=120 ft
L1=180 ft
Elevation
Max Level
Min Level
Diameter
Node 2
Pipe 8: L1 + L2 = 300 ft
Notes: Globe is most used.

## Slide 24: Extended period simulation
EPANET and similar programs find steady-flow solutions
Extended period simulation produces a sequence of steady states with approximations for:
  Tanks drain and fill
  Pressures can change at beginning and end of a time interval
  Pump operating points moving along a pump curve

## Slide 25: Uses
Extended period simulation used for:
  Modeling pressure in systems during changing demand –usually at hourly time scale
  Storage tank operation and sizing
  Water quality simulation
    EPANET can approximate water quality from multiple sources – has uses in
      Water age in system
      Detection of intrusions into a system
      Severity of contamination (impact assessment)

## Slide 26: How implemented?
In EPANET assign a demand pattern to a node
Set simulation times
Program then follows the pattern

## Slide 27: Modeling Protocol
Sketch a layout on paper
Identify pipe diameters; length; roughness values
Identify node elevations; demands
Supply reservoir (or tank); identify reservoir pool elevation
Identify pumps; pump curve in problem units
Identify demand pattern(s) and tank operating considerations
Notes: Globe is most used.

## Slide 28: example

## Slide 29: Illustrate by example

## Slide 30: Illustrate by example

## Slide 31: Illustrate by example

## Slide 32: Illustrate by example
Build network layout
  Nodes (junctions, tanks, reservoirs)
  Links (pipes, pumps, valves)
Add pump curves
  BROWSER/DATA/CURVES/ADD (TYPE=PUMP)
Add storage curves
    BROWSER/DATA/CURVES/ADD (TYPE=STORAGE)
Add demand pattern(s)
      BROWSER/PATTERNS/ADD

## Slide 33: Illustrate by example

## Slide 34: Illustrate by example

## Slide 35: Illustrate by example

## Slide 36: Illustrate by example

## Slide 37: Illustrate by example

## Slide 38: Report output

## Slide 39: Report output

## Slide 40: Report output

## Slide 41: Report output

## Slide 42: Report output

## Slide 43: Report output

## Slide 44: Next time
Water Quality in EPANET