CE 3372 Water Systems Design

Exercise Set #5

Three problems using USEPA-NET modeling program.   Each problem is a network of successive complexity introducing a different hydraulic component.  The problems should be solved in order so the first problem is a framework for the second and so on.

1. Compute the discharge in each pipe and the pressure at each junction node for the

8-pipe system shown in Figure 1. The water surface elevation in the storage tank is

315.0 ft. Prepare your solution using EPA-NET. Report your results in U.S. Customary

units.

Figure 1.  Problem 1 Network Layout

The pipe and demand data are as supplied in the problem statement.   The next several pages are an annotated output report and a screen capture to illustrate a successful model.

This particular problem explores a simple network with nodal demands (in GPM converted to CFS for the program) and a single supply reservoir.

### HEADER REMOVED FOR BREVITY ###

Input File: exercise005-1-1.net

Link - Node Table:

----------------------------------------------------------------------

Link           Start          End                Length  Diameter

ID             Node           Node                   ft        in

----------------------------------------------------------------------

1              2              3                    4000        10

2              3              4                    6000        10

3              2              5                    6000        12

4              3              6                    6500        24

5              4              7                    7000        10

6              5              6                    3000        18

7              6              7                    5000        10

8              9              3                     300        12

Node Results:

----------------------------------------------------------------------

Node                Demand      Head  Pressure   Quality

ID                     CFS        ft       psi

----------------------------------------------------------------------

2                     1.11    284.88     49.78      0.00

3                     1.11    292.57     48.77      0.00

4                     1.11    258.00     40.29      0.00

5                     3.33    284.86     56.27      0.00  <<< demand at a node

6                     2.22    286.92     59.33      0.00

7                     3.33    249.00     45.06      0.00

9                   -12.21    315.00     58.50      0.00 Tank

Link Results:

----------------------------------------------------------------------

Link                  Flow  VelocityUnit Headloss    Status

ID                     CFS       fps    ft/Kft

----------------------------------------------------------------------

1                    -1.18      2.15      1.92      Open

2                     2.06      3.79      5.76      Open

3                     0.07      0.08      0.00      Open

4                     7.86      2.50      0.87      Open

5                     0.95      1.75      1.29      Open

6                    -3.26      1.85      0.69      Open

7                     2.38      4.36      7.58      Open

8                    12.21     15.55     74.78      Open  <<< flow from reservoir IN

Figure 2.  Problem 1 screen capture.  Node values are pressure in PSI, link values are flows in CFS.

2. The pipe network in problem 1 is expanded to a 14-pipe system and includes a ground level reservoir near junction node 4 as depicted in Figure 2. A pump is installed in an 18-inch diameter pipe extending 500 feet from the ground-level reservoir (WSE = 155 ft.) to junction node 4. A booster pump pushes water into the network; three points on the pump curve are listed below. Compute the flow in each line and the pressure at each junction node. Report your results in U.S. Customary units.

Figure 3.  Problem 2 network topology

The pipe and demand data are as supplied in the problem statement.   The input data are repeated in the annotated modeling report.  A screen capture is included to illustrate a successful model run.

This problem extends the previous problem, introduces a second reservoir with water boosted into the system by a pump.   It requires the creation of a pump curve in EPA-NET.

###HEADER REMOVED ###

Input File: exercise005-2-1.net

Link - Node Table:

----------------------------------------------------------------------

Link           Start          End                Length  Diameter

ID             Node           Node                   ft        in

----------------------------------------------------------------------

1              2              3                    4000        10

2              3              4                    6000        10

3              2              5                    6000        12

4              3              6                    6500        24

5              4              7                    7000        10

6              5              6                    3000        18

7              6              7                    5000        10

8              9              3                     300        12

9              12             5                     500        18

10             5              8                    4000        10

11             6              10                   4000        24

12             7              11                   4000        12

13             8              10                   3000         8

14             10             11                   5000        12

15             1              12                   #N/A      #N/A Pump

Node Results:

----------------------------------------------------------------------

Node                Demand      Head  Pressure   Quality

ID                     CFS        ft       psi

----------------------------------------------------------------------

2                     1.11    311.58     61.35      0.00

3                     1.11    311.30     56.89      0.00

4                     1.11    292.89     55.42      0.00

5                     3.33    317.21     70.29      0.00

6                     2.22    310.67     69.62      0.00

7                     3.33    291.30     63.39      0.00

----------------------------------------------------------------------

Node                Demand      Head  Pressure   Quality

ID                     CFS        ft       psi

----------------------------------------------------------------------

8                     1.11    309.55     62.63      0.00

10                    2.22    309.47     60.43      0.00

11                    1.11    294.75     56.22      0.00

12                    0.00    321.41    139.27      0.00  << HIGH PRESSURE

1                   -11.73    155.00      0.00      0.00 Reservoir

9                    -4.92    315.00     58.50      0.00 Tank

Link Results:

----------------------------------------------------------------------

Link                  Flow  VelocityUnit Headloss    Status

ID                     CFS       fps    ft/Kft

----------------------------------------------------------------------

1                     0.20      0.38      0.07      Open

2                     1.50      2.74      3.07      Open

3                    -1.31      1.67      0.94      Open

4                     2.52      0.80      0.10      Open

5                     0.39      0.71      0.23      Open

6                     5.92      3.35      2.18      Open

7                     1.69      3.09      3.87      Open

8                     4.92      6.26     12.34      Open

9                    11.73      6.64      8.39      Open  << HIGH Q and V

10                    1.17      2.15      1.92      Open

11                    4.53      1.44      0.30      Open

12                   -1.26      1.60      0.86      Open

13                    0.06      0.18      0.03      Open

14                    2.37      3.02      2.94      Open

15                   11.73      0.00   -166.41      Open Pump

Figure 4.  Problem 2 screen capture.  Values at nodes are pressures in PSI, values at links are flow in CFS.

3. The pipe network in problem 2 is expanded to a 24-pipe system depicted in Figure 3. The water levels in the two elevated storage tanks are 315 ft. The water levels in the two ground-level reservoirs are 155 ft. The pump characteristics for the new pump in line 17 are the same as the existing pump in line 9. Compute the flow in each line and the pressure at each junction node. Report your results in U.S. Customary units.

Figure 5.  Problem 3 pipe network topology

The pipe and demand data are as supplied in the problem statement.   The input data are repeated in the annotated modeling report.  A screen capture is included to illustrate a successful model run.

This problem adds tanks and another pump.   Pump link direction is important.   A second pump curve is entered as is storage tank information.   In this example the tanks are taken as static water sources;  in practical models, we would also specify volume/depth information for computing fill/drain behavior in an extended period simulation (the subject of project 1).

####HEADER REMOVED FOR BREVITY #####

Input File: exercise005-3-A.net

Link - Node Table:

----------------------------------------------------------------------

Link           Start          End                Length  Diameter

ID             Node           Node                   ft        in

----------------------------------------------------------------------

1              2              3                    4000        10

2              3              4                    6000        10

3              2              5                    6000        12

4              3              6                    6500        24

5              4              7                    7000        10

6              5              6                    3000        18

7              6              7                    5000        10

8              9              3                     300        12

9              12             5                     500        18

10             5              8                    4000        10

11             6              10                   4000        24

12             7              11                   4000        12

13             8              10                   3000         8

14             10             11                   5000        12

16             4              13                   6000        18

17             7              13                   6000        18

18             13             19                    500        24

19             8              14                   5000        12

20             10             15                   5000        12

21             14             15                   3000        10

22             22             10                    300        12

23             11             16                   3000        12

24             16             17                   3000        12

25             16             18                   1000         6

15             1              12                   #N/A      #N/A Pump

26             20             19                   #N/A      #N/A Pump

Node Results:

----------------------------------------------------------------------

Node                Demand      Head  Pressure   Quality

ID                     CFS        ft       psi

----------------------------------------------------------------------

2                     1.11    314.77     62.73      0.00

3                     1.11    314.65     58.34      0.00

4                     1.11    322.61     68.29      0.00

5                     3.33    319.81     71.41      0.00

6                     2.22    314.42     71.24      0.00

7                     3.33    308.15     70.69      0.00

8                     1.11    309.53     62.63      0.00

10                    2.22    313.62     62.23      0.00

11                    1.11    297.89     57.58      0.00

12                    0.00    323.70    140.26      0.00 << high pressure at left pump

13                    2.22    326.82     65.79      0.00

14                    1.11    307.72     57.51      0.00

15                    1.11    308.18     55.54      0.00

16                    0.00    278.39     51.30      0.00

17                    3.33    261.19     48.18      0.00

18                    0.22    277.35     50.85      0.00

19                    0.00    327.38     66.02      0.00

1                   -11.29    155.00      0.00      0.00 Reservoir

20                   -8.90    155.00      0.00      0.00 Reservoir

9                    -1.48    315.00     58.50      0.00 Tank

22                   -2.97    315.00     58.50      0.00 Tank

Link Results:

----------------------------------------------------------------------

Link                  Flow  VelocityUnit Headloss    Status

ID                     CFS       fps    ft/Kft

----------------------------------------------------------------------

1                     0.13      0.24      0.03      Open

2                    -0.97      1.78      1.33      Open

3                    -1.24      1.58      0.84      Open

4                     1.47      0.47      0.04      Open

5                     1.22      2.24      2.07      Open

6                     5.36      3.03      1.80      Open

7                     0.94      1.73      1.25      Open

8                     1.48      1.88      1.17      Open

9                    11.29      6.39      7.78      Open  <<high Q and V at left pump

10                    1.37      2.50      2.57      Open

11                    3.66      1.17      0.20      Open

12                    2.21      2.81      2.57      Open

13                   -0.54      1.56      1.36      Open

14                    2.45      3.12      3.15      Open

16                   -3.30      1.87      0.70      Open

17                   -3.38      1.91      3.11      Open

18                   -8.90      2.83      1.11      Open

19                    0.80      1.02      0.36      Open

20                    1.42      1.81      1.09      Open

21                   -0.31      0.57      0.15      Open

22                    2.97      3.79      4.59      Open

23                    3.55      4.52      6.50      Open

24                    3.33      4.24      5.73      Open

25                    0.22      1.12      1.04      Open

15                   11.29      0.00   -168.70      Open Pump

26                    8.90      0.00   -172.38      Open Pump

Figure 6.  Exercise 3 screen capture.   Node values are pressure in PSI;  Link values are flow in CFS.