## Slide 1: CE 3372 Water Systems Design
Lecture 23: EPA SWMM– Storage Nodes and Detention Basins

## Slide 2: Purposes
Detention Basin
Storage Node

## Slide 3: Junction (Node)
Ordinary junction connects hydraulic elements (links)
Junction attributes are:
  Invert elevation (elevation of the bottom of the node)
  Max elevation (elevation of top of node)
    Set to land surface to plot profile grade line in SWMM
    Set to land surface + added depth for dual (surface+subsurface drainage)
When program runs, depth at the node is computed, but there is no storage (node has zero area)

## Slide 4: Junction (Node)
Ordinary junction just connects pipes N-1, N, and N+1

## Slide 5: Junction (Node)
If flooding occurs, it is only considered when HGL is above node Max. Depth
Node not flooded; pipes are surcharged
Node flooded; pipes are surcharged

## Slide 6: Flooding Ordinary Node

## Slide 7: Junction (Node)
Flooded node attributes:
  How deep is the flooding allowed (surcharge depth) above the top of the node
  What is the ponded area during surcharge – treats the node as a vertical wall storage tank
Ponded Area
Ponded Depth
Max. Depth
Invert Elevation
Invert Elevation + Max. Depth

## Slide 8: Storage Unit (Node)
A storage node explicitly considers storage in the node – including (if data are correctly supplied) the sub-grade portion of the node
Storage Node Attributes
  Same as an ordinary node +
  Depth-Area relationship
    Tabular
    Functional

## Slide 9: Storage Unit (Node)
Useful for:
  Detention ponds
  Modeling multiple level inlet/outlet hydraulics
    Riser inlet
    Outlet that has portion through a pipe, a portion over a weir (or another pipe at different elevation)

## Slide 10: Example
Consider a detention pond that drains a 5-acre parking lot, then discharges to a nearby receiving stream
Use SWMM to approximate the hydraulics
  Sub-catchment, high CN (98) to represent the parking lot
  1-inch/hour storm for 3 hours
  All flow passes through the detention pond before exiting to a stream through a 6-inch pipe at the inverts, and a 1-foot pipe at 2-feet above basin bottom

## Slide 11: Example
Schematic of the system
5 acre; CN=98
1 inch/hr for 3 hrs
Detention Pond
1 foot pipe
6-inch pipe
Ordinary Node
Outfall
Large Diameter Pipe to connect to outfall without surcharge

## Slide 12: Detention Pond Drawing

## Slide 13: Depth-Area
Use the drawing to determine the depth-area of the pond
  Pick an elevation (depth)
  Find pool area for that elevation (depth)
  Record the depth and the area (in acres usually)

## Slide 14: Depth-Elevation
Pool elevation = 140 ft.
Depth = 0.5 ft.
Pool Area = 0.25 acres

## Slide 15: Depth-Elevation
Pool elevation = 141 ft.
Depth = 1.5 ft.
Pool Area = 0.35 acres

## Slide 16: Depth-Elevation
Pool elevation = 142 ft.
Depth = 2.5 ft.
Pool Area = 0.55 acres

## Slide 17: Depth-Elevation
Pool elevation = 143 ft.
Depth = 3.5 ft.
Pool Area = 0.70 acres

## Slide 18: Depth-Elevation
Pool elevation = 144 ft.
Depth = 4.5 ft.
Pool Area = 0.90 acres

## Slide 19: Depth-Elevation
Pool elevation = 145 ft.
Depth = 5.5 ft.
Pool Area = 1.20 acres

## Slide 20: Depth-Elevation
Pool elevation = 148 ft.
Depth = 8.5 ft.
Pool Area = 1.85 acres
Any deeper and we are inundating off-site property

## Slide 21: SWMM Model Run
Peak Q from the parking lot
Peak Q leaving the detention pond

## Slide 22: Next Time